# The Scottish Public Sector Data Hosting and Data Centre Efficiency Assessment Tool

# User Guide

July 2016

Version 1.0

- Contents

1.	Preface	2

Preface by Scottish Government	2

2.	The Purpose of the Scottish Public Sector Data hosting and Data Centre Efficiency Assessment Tool	2

Data Centre Efficiency	2

Total Cost of Ownership	2

ICT Service Delivery	3

Scenarios	3

3.	When should you use it	3

4.	Who should use it	3

5.	How you can use it	3

Running the tool	3

Step 1: Enter information about your organisation	4

Step 2: Data Centre Detail	5

Step 3: ICT Requirements	11

Step 4: Review the results	14

Step 5: Save the results	15

Optional Step: Clear Data	16

6.	Appendix A: Power Utilisation Efficiency	17

Appendix B: Total Cost of Ownership	18

Appendix C: Data Collection Templates	19

Data Collection Form A: Organisation Information	19

Data Collection Form B: Data Centre Description and Contents	20

Data Collection Form C: Data Centre Power Consumption	22

Data Collection Form D: Infrastructure Staff Costs	25

Data Collection Form E: Organisation ICT Requirements	26

Data Collection Form F: ICT Services	27

Acronyms	30

# Preface

## Preface by Scottish Government

Scotland’s public sector data hosting strategy published in April 2014 sets a vision that Scotland's public sector data hosting is cost-effective, carbon neutral and makes appropriate use of cloud technology, for the delivery of efficient and highly available ICT services.

To supplement the existing guidance on cloud, co-location and virtualisation available to public sector organisations for their hosting solutions this tool will help identify existing costs including energy consumption.

In line with Government policy to reduce the number of data centres in the public sector this tool will help organisations through a consistent approach identify alternative solutions. The visual results will provide a high level indication of where efficiencies and savings can be made by highlighting appropriate greener and cheaper solutions based on the data that’s input.

This Data hosting and Data centre efficiency assessment tool will provide public sector organisations with additional evidence to support high level business cases which when aligned with the principles of the strategy will encourage organisations to consider moving to more efficient and economical solutions.

# The Purpose of the Scottish Public Sector Data hosting and Data Centre Efficiency Assessment Tool

This tool has been devised to assist Scottish Public Sector organisations to understand the efficiency of their data centres, their total cost of ownership and options available for changing the way their ICT services are delivered.

## Data Centre Efficiency

The efficiency of data centres is typically measured using the Power Utilisation Efficiency (PUE); the same measure can also be applied to server rooms in integrated buildings.  This is described in more detail in Appendix A.  This model allows the PUE of up to four data centres used by an organisation to be assessed on a current, three year and five year basis.

In order to calculate PUE to a good level of accuracy, metered energy data is required for both the ICT equipment and for the whole facility.  In many Public Sector data centres and server rooms, the required metering is not present.  This model allows the energy consumption to be estimated provided that the types of ICT equipment and associated lighting, power distribution and cooling equipment are known.

## Total Cost of Ownership

The total cost of ownership (TCO) of a data centre incorporates both ICT and non ICT costs associated with that data centre.  A detailed description of TCO is provided in Appendix B.

This model allows for costs relating to buildings, hardware, maintenance, networks, utilities and staff to be collated on a current year, three year and five year basis.   Where possible, the model provides default costs that may be used when actual cost data is unavailable.

## ICT Service Delivery

Once the efficiency and total cost of ownership of an organisation’s ICT infrastructure are understood, it is possible to evaluate options for improving efficiency and reducing costs.  This model allows options such as technology improvements, co-location and transfer to the cloud to be investigated.  The model uses cost data based on the frameworks available to public sector organisations.

## Scenarios

Finally, the model allows up to six scenarios to be saved.  This allows different business cases to be evaluated and periodic assessments of efficiency and cost to be made.  For example, improving the efficiency of an existing data centre could be compared to co-locating into a third party data centre or the performance of a data centre could be compared year on year.

# When should you use it

The first use of the tool should set a baseline for your organisation’s ICT provision costs and data centre efficiencies.  You can then use the tool in two ways:

- To test various scenarios such as improving the efficiency of one of your data centres, co-locating some of your servers or transferring some of the ICT provision to the cloud.

- To record the performance of your ICT services and data centres at regular intervals.

The tool allows you to save up to 6 different scenarios.  If you want to save more than 6 scenarios, you can save a separate version of the spreadsheet.

# Who should use it

Whilst an individual with in the organisation should be assigned to “own” the model, a variety of individuals from different sections of the organisations will need to contribute data to that individual.

The model requires a combination of the following information:

- Current ICT service provision

- Data centre technical information

- Data centre financial information

Typically, a team comprising individuals from ICT, facilities management or estates and finance will be required to carry out a full analysis of an organisation’s ICT infrastructure and service provision.

# How you can use it

This section provides guidance on how to enter data into the tool and how to interpret the results.

## Running the tool

This tool has been devised to run in Excel 2010 and later editions.  It needs to have macros enabled to function correctly.  This is achieved by selecting ‘enable content’ on the top bar when prompted to do so.  If this option is not available, the macro settings can be changed by selecting ‘Options’ on the ‘File’ menu and then selecting the ‘Trust Center’ option.  You will find the macro settings under the ‘Trust Center Options’ where you will need to select ‘Macro Settings’ on the right hand menu bar.  You should select ‘Disable all macros with notification’. This setting ensures the macros are disabled but still each time when you open an excel sheet with a macro it will ask you if you want to run the macro or not.

You will be prompted to follow a series of steps, each requiring you to either enter data or review results.  Data should only be entered into the yellow shaded cells, if you try and enter data into other cells an error message will be displayed.  You can navigate to different pages in the model using the buttons on the ‘Introduction’ tab.

There are five steps required to complete the tool as follows:

Each of these steps is explained in more detail below.  Appendix C contains templates to assist the collection of the data required for the tool.

## Step 1: Enter information about your organisation

Basic information on your organisation and the scenario that you would like to run should be entered in this section along with utility cost information.  Your electricity and natural gas tariffs can usually be sourced from your energy manager or estates department.  The escalation rates determine how the utility costs will be increased when looking at the likely performance and cost of your data centres in three or five years’ time.  ‘Real’ escalation rates should be used i.e. they should represent the likely annual increase in prices above normal inflation.  For example, over the last ten years’ electricity prices have gone up on average 12% per year.  If the average inflation rate over the last ten years was 2%, the real inflation rate that should be entered would be 10%.  Your finance department should be able to help you determine appropriate values to enter into this section.

## Step 2: Data Centre Detail

You can enter information on up to four data centres.  These can either be data centres owned by your organisation, space rented in other buildings or data centres or racks rented in other data centres.

### Data Centre Information

Information on each data centre’s location, type, ownership and size should be entered.  The location should be selected from a drop down list.  If the data centre’s location is not given in the list, the nearest town should be selected.  It is very important that the floor area is filled in for owned or leased data centres as it is used for cost estimation if actual cost data is not available.

The options for ownership are ‘owned’, ‘leased’ and ‘racks leased’.  ‘Leased’ refers to the situation where your organisation leases a building or part of a building. ‘Racks Leased’ refers the lease of individual racks within a building, with no responsibility for the building itself.

### Data Centre Rating and Disaster Recovery

The next section allows general information concerning the data centre to be collated such as the tier rating and % availability.  The stated PUE should be entered if known.  This is essential for where a co-located data centre is used and the actual energy usage is not known.

### Rack and Server Information

The number of racks, their utilisation and the devices that they host are entered in this section.  Servers, storage devices, network devices, ancillary devices and any other devices can be recorded. The servers should be classified as follows:

| Server Size | Typical Configuration |
| --- | --- |
| Small | 1 core, 4GB RAM, 100GB Storage |
| Medium | 2 core, 8GB RAM, 200GB Storage |
| Large | 3 core, 12GB RAM, 400GB Storage |
| Extra Large | 4 core, 16GB RAM, 800GB Storage |

Any more unusual devices can be recorded under the ‘Other’ category.

### Estimation of ICT Load

In most larger data centres, the ICT power is likely to be separately metered.  In smaller server room or older data centres, this may not be the case.  Where metered data is not available, the model estimates total ICT load by multiplying the number of each type of server or other device by the average consumption for that device.

Where ICT power is separately metered, the point of measurement should be selected.  The options are: after UPS; after PDU; or at equipment.  If the measurement point is on the output from the UPS, the losses due to the PDU will need to be entered as the energy associated with these losses will be deducted from the measured ICT power for the purposes of PUE calculation.  The PDU losses will be dependent on the type of PDU and its level of utilisation, but can range from 1% to 10%.

Where ICT power is not separately metered, estimated average consumption of the different types of devices in the data centre should be entered:

For each category of ICT load type, server (small, medium, large, very large), storage, network and other, enter the consumption in kWh for a typical device.  Guidance on typical consumption levels is given below:

#### Servers

IBM provided the following estimate of server energy consumption in 2011:

- 1U rackmount x86: 300 W-350 W

- 2U rackmount, 2 socket x86: 350 W-400 W

- 4U rackmount, 4 socket x86: average 600 W, heavy configurations 1000 W

- Blades: average chassis uses 4500 W; divide by number of blades per chassis

To estimate within these ranges, consider that electrical consumption increases with higher clock-speed CPUs, larger numbers of memory cards such as DIMMs and physical disks, and with greater processor utilization.

Servers that don’t fall into one of the listed categories can have typical power estimated by multiplying the nameplate rating by 70 per cent. This estimation is reasonable only for a large population of servers, such as a whole data centre. It’s not accurate with any granularity, and certainly not at the single-server level.

#### Storage

Your electricity consumption related to your storage devices will depend on the type and size of storage and the level of utilisation.

- Storage controllers can use around 200W

- Disk enclosures can use 150 – 200W

- Disks typically range from 2 – 15W

#### Network

Network devices can vary from a few W to kW depending on their type and scale.

#### Other

If you have any other devices, such as a legacy mainframes or a VDUs you will need to assess their average power consumption.

### Total Utilities to Data Centre/Server Room

Once the total ICT load has been entered, the total power to the facility should be entered.  Where this is separately measured, the measured quantity should be entered.  In should also be noted whether the measured amount includes any power generation from backup generators.  Where the measured total power is recorded by a utility meter, the generator power will not be included.

Where the total power is not metered, but some elements of the power consumption are sub metered, these can be entered separately.

Any natural gas or water used should also be recorded.

### Estimation of Power

The next section allows the consumption related to lighting, UPS, PDU, HVAC and other electrical equipment to be assessed.  It also allows generator output to be entered or estimated.  For each different type of power consumption, you have the choice of:

- Entering the type of equipment and allowing the spreadsheet to estimate the power consumption based on defaults

- Using any metered data entered

- Entering your own estimate of usage.  This will override both estimated power and measured consumption

Where the third option is chosen, it is recommended that you record the calculation methodology used for the estimate.

The following screenshot shows the data entry for lighting energy:

The following defaults are used by the model:

#### Lighting

The following table shows the options that can be selected for the types of lighting used and the default consumption in W/m2 used by the model for each option:

| Type | W/m2 |
| --- | --- |
| LED | 4 |
| T12 Fluorescent | 30 |
| T8 Fluorescent | 13 |
| T5 Fluorescent | 7 |
| Compact Fluorescent | 8 |
| Other | 15 |

The lighting controls can also be selected.  The following options and percentage reductions in lighting energy assumed for each by the model are used:

| Type | % |
| --- | --- |
| Manual | 50% |
| 24x7 | 100% |
| Motion controlled dimming | 10% |
| Motion controlled switch off | 10% |

#### UPS

Three different efficiencies of UPS can be selected or, where no UPS is present, ‘None’ can be selected:

| Type | % |
| --- | --- |
| None | 100% |
| Low Efficiency (85%) | 85% |
| Typical (90%) | 90% |
| High Efficiency (95%) | 95% |

#### HVAC

The following equipment types can be selected:

HVAC Equipment Type

Air cooled single unit

Split unit/DX-glycol unit

Chilled water cooling tower

Chilled water cooling tower with VSD

Chilled water with dry cooler

Chilled water with dry cooler with VSD

Chilled water with packaged chiller

It is also necessary to specify whether cooling is delivered directly to the racks (‘close coupled’) or is delivered to the surrounding area (‘perimeter’) and whether an air side economiser is present (an air side economiser uses outside air to provide cooling when temperature and humidity conditions are suitable, often known as free cooling).  Finally, the percentage utilisation of the HVAC equipment should be entered.

#### PDU

The percentage PDU losses should be entered.  As discussed above, these are typically between 1% and 10%. The model uses 10% if no other information is provided.

#### Other

The model assumes that a further 2.5% of ICT energy is used by other systems such as fire suppressant and monitoring.

### Generator Energy

The default power generated by the generator is calculated by taking its capacity in kW and multiplying it by the number of full load hours that it runs.  For example, if the generator runs for one hour on full load and then four hours on 50% load, this would be equivalent to running at full load for three hours.  The generator hours will be dependent on the testing regime used.  Typically, they will be tested for at least one hour at least once per month.

### PUE Calculation

Once the data above has been entered, the PUE is calculated for each of the three years entered.

### Data Centre Costs

Once the technical details of the data centre have been added, the cost data should then be entered.  Your finance department may need to supply some of the required information.

#### Utility Costs

These are calculated automatically from data already entered.

#### Data Centre Infrastructure Staff Costs

Any staff costs associated with running the data centre should be entered.  Staff costs associated with the services delivered from the data centres should not be included.  These costs can either be added as an annual total, if known, or by entering the number of staff and the average annual cost of a member of staff.  If the average annual cost of a staff member is not known, the model uses a default of £35,000.

#### Communication Costs

Costs for communications networks should be entered in this section.  This includes payments to comms network providers.

#### Building Costs

Rates, insurance, maintenance, rent and other building costs should be entered in this section.  For rates, insurance and maintenance, defaults are provided if no other information is available.  Rateable values are based on £95/m2 for data room floors, £130/m2 for office areas and £65/m2 for ancillary areas.  Rates are payable at a rate of £0.45 per £ of rateable value.  Insurance is set at £3/m2 and maintenance at £5/m2.  Where your organisation rents racks in a data centre, no information should be entered in this section.

#### Licensing and Maintenance

Hardware maintenance and cabling costs should be entered in this section.  Hardware maintenance refers to the cost of maintaining existing servers and devices, not replacing them.  The default assumption is that 15% of the initial cost of a device is required each year for maintenance.  Costs for server and software licenses should be entered in the next section.  If none are entered, a default of £1,000 per server is used.  These are likely to vary widely from organisation to organisation so should be assessed in some detail to find actual costs.

#### Hardware and Hosting

The costs of replacing servers and other devices should be entered into this section.  The default assumption is that each device should be replaced every five years.  The estimated cost of each type of devices is shown in the following table:

| Servers | Cost |  |
| --- | --- | --- |
| Small | £ 900 | per device |
| Medium | £ 2,000 | per device |
| Large | £ 10,000 | per device |
| V Large | £ 40,000 | per device |
| Storage | £ 2,500 | per TB |
| Network devices | £ 2,500 | per device |
| Ancillary devices | £ 5,000 | per device |

Where your organisation rents racks in a data centre, these should be entered in the hosting costs section.

#### Other Costs

There may be other costs associated with the data centre that are not covered by the sections above.  These can be entered in this section.

#### Income from Hosting

Where other organisations have collocated in a data centre belonging to your organisation, any income can be entered in this section.

### Total Cost of Ownership

The data entered above is used to calculate the total cost of ownership for each of the three years for each data centre.  This cost of ownership is net of any income received for hosting for third parties.

## Step 3: ICT Requirements

The next tab on the spreadsheet allows details about the services being delivered by the organisation’s ICT infrastructure to be entered.  This involves two distinct parts: the staffing requirements and the services themselves.

### Staffing Costs

The staffing costs solely associated with the data centres entered into the previous tab will be reflected in the staff costs table.  Other staff costs associated with ICT provision should be entered, either by entering the actual staff costs or by entering the number of staff and the average annual salary cost.

### Other Communication Costs

Your organisation may have communication costs not associated with data centres, for example it may make payments to comms network providers for lines to local offices.  These can be entered in this section.

### ICT Services Provided

This section allows up to ten different ICT services to be added and costed.  An example of an ICT service would be ‘Business Systems on Legacy Servers’ or ‘Web Hosting on Virtualised Servers”.  For each service data on how it is currently hosted, any restrictions on hosting locations or security and transition costs are requested.  This information is used to estimate what the cost of transferring provision of the service to co-located servers or to the cloud.

#### Service Description

This section requires a short description of the service, such as ‘email provision’ or ‘finance system’ and how it is currently provided.  The options for current provision are:

- Server in own datacentre

- Co-located server

- Virtualised server in own datacentre

- Virtualised co-located server

- Private Cloud

- Public Cloud

- Other

The other option should be selected for managed services, software as a service and other similar service types.

#### Server Requirements

The next section requires the number of racks and servers dedicated to delivering the service to be entered.  It also requires the data centre that the service is delivered from to be entered.  Where a service is delivered from more than one data centre, separate entries should be made for each.  When entering racks and servers, fractions are permitted.  The servers should be categorised by size.

#### Storage Requirement

Where a service requires storage, three different types can be specified: Performance Storage, Standard Storage or Archive Storage.  The total GB of storage required in each category should be entered.

#### Comms Requirement

The total bandwidth in Mbps required for delivery of the service should be entered in this section.

#### Security

The number and type of digital certificates required for delivery of the service should be entered.  The current cost of provision of these certificates should also be entered.  In addition, the number of firewalls required should be entered.

#### Backup

The backup type should be selected. Depending on the type of back up used, either the number of tapes or the required backup GB should be entered.

#### Other Information

This section allows any restrictions related to legacy servers and any other costs to be entered.  These other costs may be annual software license costs, co-location costs and annual service costs.

#### Location and Security Restrictions

Any location constraints on data hosting or application hosting should be entered.  The options are Scotland, UK, Europe or Any.  If regular physical access to the servers by your organisation’s ICT staff is required, ‘Yes’ should be selected.  If physical access is required, the cloud options will not be considered in the options appraisal and the co-location options will not be considered for the Western Isles, Orkney or Shetland.   It is assumed that co-location is possible in all other locations.  Finally, if you enter ‘Yes’ to the ‘Other restriction to relocating servers’ then no other options will be considered.  You may need to use this option if you have equipment such as a print server in a local office.

The security type of the data should be entered.  The options are ‘Official’, ‘Secret’ and ‘Top Secret’.  If there are any restrictions on storing data in the cloud, ‘Yes’ should be selected.  This will ensure that the cloud options are not considered in the options appraisal.

#### Cost Information

If the transition cost for transfer of servers to a co-location data centre are known or can be estimated, these should be entered.  Similarly, the transition cost for transferring a service to the cloud should be entered if known.

If your organisation plans to make any changes to staff numbers on transfer of a service to a co-located data centre or the cloud, these should be entered.

If your organisation has already evaluated alternative options for hosting the service, the cost of this can be recorded under the ‘Cost of any Custom Solution’.

## Step 4: Review the results

The results can be reviewed using the available reports:

| Report Name | Description |
| --- | --- |
| Data Centre Report | A graphical representation of the PUE and TCO for each data centre |
| Options Report | A summary of the current cost of provision of the ICT services and of options for their replacement |
| Summary Report | A high level summary of all results for the scenario |
| Scenario Report | A summary of all scenarios |
| Assumptions Report | A summary of the assumptions for a scenario |

### The Data Centre Report

This report shows the power utilisation efficiency (PUE) and the total cost of ownership (TCO) of each data centre.  It also gives an indication of the quality of the PUE calculation.

The total cost of ownership represents all costs associated with each data centre.  It only includes staff costs associated with the data centre operation, not the total cost for all ICT staff.

The PUE is the ratio between the total power used by the facility and the power used directly by the ICT equipment.  It will be an integer between 1 and approximately 4.  A result in the range 1 – 1.6 indicates an efficient data centre and a result over 2.4 indicates that the data centre has poor efficiency.

The quality of the calculated PUE is indicated by a Red, Amber, and Green graphic.  Where all facility power and ICT power is separately metered, Green status is achieved.  Where some of the power is metered the quality will be rated Amber and when the majority of the power usage is estimated, it will result in a Red status.

The graphs at the bottom of the report show the number of racks and different types of device in each data centre.

### The Options Report

This report shows the cost of provision of each service entered into the tool.  Where the service is delivered from one of the data centres entered into the tool, an average cost per server for that data centre is used to determine costs.

The co-location and cloud options are costed using structures and pricing that is in line with the Scottish Government Data Hosting Procurement Framework.  The preferred option is selected based on the most economic option possible within any security or location constraints selected.

### The Summary Report

This report provides a summary of the information given in the Data Centre Report and the Options Report.  It provides a one-page snapshot of the organisations performance and options.

### The Scenario Report

This report summarises the results of the current scenario and of the six saved scenarios.  It provides two separate tables, one detailing the data centre results and the other the options analysis.

### The Assumptions Report

This report can be used to review all the assumptions made for a scenario.  The scenario is selected by using the drop down at the top of the report.

## Step 5: Save the results

The model allows up to six scenarios to be saved for future reference.  The six scenarios are shown on the ‘introduction’ tab.  To save a scenario, select which position to save it to and click the ‘Save Scenario’ button.  Any existing data for that scenario will be overwritten.

## Optional Step: Clear Data

All existing data for the current scenario can be cleared by clicking the ‘Clear Current Data’ button.

# Appendix A: Power Utilisation Efficiency

The PUE calculation is made up of two elements as follows:

PUE= Total Facility PowerICT Equipment Power

This is demonstrated in the following diagram:

# Appendix B: Total Cost of Ownership

The following diagram shows the elements that make up the total cost of ownership of a data centre.

# Appendix C: Data Collection Templates

## Data Collection Form A: Organisation Information

### Organisation Information

| Organisation name |  |
| --- | --- |
| User name |  |
| User email |  |
| No of ICT users |  |
| No of data centres |  |

| ### Utility costs |  |  |
| --- | --- | --- |
| Electricity |  | p/kWh |
| Natural Gas |  | p/kWh |
| Generator Fuel |  | p/kWh |
| Water |  | £/m3 |

| ### Utility Escalation Rates |  |
| --- | --- |
| Electricity | % |
| Natural Gas | % |
| Generator Fuel | % |
| Water | % |

## Data Collection Form B: Data Centre Description and Contents

Fill one of these in for each data centre

### General Information

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Name |  | The name you normally use for the data centre |
| Location |  | The nearest town or city to the data centre |
| Standalone or integrated |  | If your data centre is in a dedicated building choose standalone, otherwise select integrated |
| Ownership |  | State whether the data centre is owned by your organisation is leased (either part or all of the building, or whether your organisation leases rack space only. |
| Data room floor area m2 |  | Floor area is required to calculate default area if you do not have measured data. |
| Office floor area m2 |  | As above |
| Ancillary floor area m2 |  | As above |

### Rating and Recovery

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Tier Rating |  | If you know the tier rating of your data centre, enter it here. |
| Actual Availability |  | If you measure availability of your data centre, enter it here. |
| Stated PUE |  | Enter any previously recorded data centre PUE or any third party data centre PUE. |
| Data Centre Disaster Recovery |  |  |
| Type |  | What type of backup service is used for the data centre – the options are network attached storage, tape, backup to another owned data centre, backup to public or private cloud or no backup provision. |
| Time to bring back service |  | Enter the number of minutes that it will take to achieve either full or partial recovery (whichever is selected below) |
| Full or partial recovery |  | Can you achieve full or partial recovery from the backup |

### Racks and Servers

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| No of racks (42u equivalent) |  | Enter the number of racks in your data centre, whether used or not. |
| Rack utilisation |  | Enter the percentage utilisation of your racks |
| No of devices |  |  |
| Servers |  |  |
| Small |  | Enter the number of physical small servers in the data centre, see the main text of the user guide for the definition of the different server sizes |
| Medium |  | As above for medium servers |
| Large |  | As above for large servers |
| V Large |  | As above for very large servers |
| Storage |  | Enter the number of storage devices such as arrays |
| Network devices |  | Enter the number of network devices such as switches, firewalls and other communication devices |
| Ancillary devices |  | Enter any other devices such as VDUs in this section |
| Other |  | You can use this for any other devices such as an old mainframe |
| Total storage capacity |  | Enter the total storage capacity in TB |

## Data Collection Form C: Data Centre Power Consumption

This section allows any measured power or estimated power to be entered.

### ICT Power

| Data Required | Enter data here |  |
| --- | --- | --- |
| Is the total ICT power separately metered? |  | If there is a meter recording the total power consumption, either after the UPS or before or after the PDU or at the equipment enter yes, otherwise enter no |

If Yes:

| Metering Point(s) |  | Indicate where the power is measured - after the UPS or before or after the PDU or at the equipment |
| --- | --- | --- |
| Total kWh/year measured |  | Enter the annual quantity measured in kWh |
| Estimated PDU Losses |  | Enter the estimated level of power distribution losses, normally 5 – 10% |

If No:

| Estimation of ICT Load |  |  |
| --- | --- | --- |
| Average small server consumption |  | Enter the average consumption for small servers in Watts |
| Average medium server consumption |  | As above for medium servers |
| Average large server consumption |  | As above for large servers |
| Average very large server consumption |  | As above for very large servers |
| Average storage device consumption |  | As above for storage devices |
| Average network device consumption |  | As above for network devices |
| Average ancillary device consumption |  | As above for ancillary devices |
| Other |  | As above for any other devices entered |

### Total Utilities to Data Centre/Server Room

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Is all non ICT power use or total power separately metered? |  | If all power to lighting, HVAC, UPS and other non ICT equipment is metered select yes. They do not each have to be metered individually, only the total power is needed. |

If Yes:

| Is generator electricity included in this metered power? |  | If the power is metered after any generator input select yes, otherwise select no. |
| --- | --- | --- |
| Total kWh/year measured including ICT Load |  | Enter the total annual electricity supply in kWh to non ICT equipment |

If No:

| Is some of the power separately measured? |  | Select yes if you have some items such as cooling or lighting sub metered. |
| --- | --- | --- |
| Measured Consumption kWh (leave blank if unknown) |  |  |
| Lighting |  | Enter measured annual consumption in kWh |
| UPS Losses |  | As above |
| HVAC |  | As above |
| PDU Losses |  | As above |
| Other |  | As above |

### Other Utility Usage

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Natural Gas (kWh) |  | If any heat is supplied to your data centre, enter the amount of natural gas used in kWh/year |
| Water (m3) |  | If any water is supplied to your data centre, enter the amount of water used in m3/year |

If the Total Facility Power is not separately metered:

In this section you can either use the default calculated by the spreadsheet or use your own estimate of energy consumption

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Lighting |  |  |
| Lighting Type |  | Select the lighting type from the list of options |
| Lighting Controls |  | If lighting controls are in place, enter the type of controls present i.e. motion controlled dimming or motion controlled switch off. Otherwise select 24x7 if the lights are always switched on or manual if they are switched off by staff. In the latter case, it will be assumed that they are on for 50% of the time |
| Or enter your own estimate |  | Enter the annual kWh consumption for lighting if you do not want to use the value calculated by the model. |
| UPS |  |  |
| UPS Type |  | Select whether you use a low efficiency, typical efficiency or high efficiency UPS. |
| Or enter your own estimate |  | The model will calculate UPS losses; enter your own estimate if you have the data in kWh per annum. |
| HVAC |  |  |
| HVAC Type |  | Select the HVAC type from the list. |
| Capacity Utilisation |  | Select how much of the cooling capacity is used. Systems running at less than 100% load are likely to be less efficient. |
| Perimeter or Close Coupled |  | If the cooling is supplied to the room along isles, select perimeter, if the cooling is supplied directly to the racks through ducts select close coupled. |
| Airside Economiser |  | If your cooling has an airside economiser fitted, enter yes. |
| Or enter your own estimate |  | Alternatively, you can enter your own estimate of cooling load in kWh per annum. |
| PDU |  |  |
| Enter your estimated losses |  | If you know your PDU losses enter them here in kWh per annum. If you do not enter them here, the losses indicated in the ICT section will be used. |
| Generator |  |  |
| Generator capacity kW |  | If you use a generator, state the rated capacity in kW |
| Generator annual hours at full load |  | Enter the average number of hours run by the generator |
| Generator Efficiency % |  | Enter the generator efficiency |
| Or enter your own estimated kWh |  | Alternatively enter your estimate of the total annual electricity generation. |
| Other |  |  |
| Enter your own estimate |  | If there is non-ICT energy consumption not already accounted for enter it here, otherwise enter £0. |

## Data Collection Form D: Infrastructure Staff Costs

Note that this section should only include staff dedicated to data centre operation, not staff supporting the servers and systems within the data centre.  For most data centres, no staff will be entered here.

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| If known, enter annual staff costs |  | Enter staff costs in £/year |
| or Enter number of staff |  | Enter the number of FTE staff |
| Enter the average annual staff salary |  | Enter the average salary level including employers NI and benefits |

### Data Centre Costs

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Network/Comms Costs |  | Enter any 3rd party communications costs associated with the data centre, for example the cost of any leased lines. |
| Building Costs |  |  |
| Enter annual rates cost |  | Enter in £/year |
| Enter annual insurance cost |  | Enter in £/year |
| Enter annual maintenance cost |  | Enter in £/year |
| Enter any rent payable |  | Enter in £/year |
| Enter any other costs |  | Enter in £/year |
| Hardware/Cabling Maintenance |  | Enter any costs associated with maintaining existing hardware and cabling in £/year |
| Licenses |  | Enter total license costs for all operating systems and software used in the data centre |
| Hardware Replacement |  | Enter estimated average annual hardware replacement costs |
| Hosting Costs |  | Enter any hosting costs that you pay the owner of the data centre (where you are renting space or rack space) |
| Enter any other costs associated with ICT Provision |  | Enter any other costs associated with the data centre that are not included elsewhere e.g. security or cleaning |

### Income from Hosting

Your data centre may receive income from space or rack space to other organisations.  If this is the case, this should be entered in this section

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Income |  | Enter in £/year |

## Data Collection Form E: Organisation ICT Requirements

### ICT Staff Costs

All of the ICT staff not dedicated to data centre operation should be included in this section

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| If known, enter annual staff costs |  | Enter in £/year |
| or Enter number of staff |  |  |
| Enter the average annual staff salary |  | Enter in £/year |

### Communication Costs

Communications costs refers to the costs of maintaining communication links between the organisations sites.

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Total Communication Costs |  | Enter in £/year |

## Data Collection Form F: ICT Services

For each ICT Service, a separate form should be filled in.  The definition of service should be tailored for your own organisation.  It could consist of services such as email provision, web hosting etc. or could be based on how the services are hosted such as virtualised servers, non-virtualised servers, backup provision etc.

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Service Name |  |  |
| How provided e.g. 3rd party data centre, managed service etc. |  |  |

### Server Requirements

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Data Centre Name |  | State which data centre the service is delivered from |
| Racks used |  | State the number of racks required |
| Server Details |  |  |
| Small |  | Enter the number of servers required |
| Medium |  | As above |
| Large |  | As above |
| Extra Large |  | As above |

### Storage Requirements

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Performance Storage GB |  | Enter the amount of storage in GB |
| Standard Storage GB |  | As above |
| Archive Storage GB |  | As above |

### Communications Requirements

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Bandwidth requirement Mbps |  | Enter the total server side bandwidth requirement |

### Security

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Digital Certificate Type |  | If you require certificates, select the type required |
| No of Certificates |  | Enter the number required |
| Total Certificate Costs (if known) |  | Enter the current annual certificate costs |
| No of Firewalls |  | Enter the number of firewalls needed |

### Backup

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Current Backup Type |  | Enter current backup storage type |
| No of Tapes |  | If you use tapes, enter the number required per year |
| Current Backup GB |  | Enter the GB backup requirement |
| Current Cloud Backup Costs |  | Enter in £/year |

### Other Information

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Legacy application requiring dedicated server? |  | Select yes if the legacy application cannot be transferred to the cloud |
| Annual software license costs |  | Enter in £/year |
| Annual co-location costs |  | Enter in £/year |
| Annual service costs |  | Enter in £/year |

### Location Restrictions

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Location constraints for data (Y/N) |  | Enter ‘any’ unless there is a location restriction |
| Location constraints for applications |  | Enter ‘any’ unless there is a location restriction |
| Regular physical access to server required |  | Enter ‘Yes’ or ‘No’ |
| Other restrictions to relocating servers? |  | Enter ‘Yes’ or ‘No’ |

### Security Restrictions

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Security constraints on cloud based system? |  | If the service cannot be delivered from the cloud, select Yes |

### Transition Costs

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Transition cost for transfer to co-location (if known) |  | Enter total cost to transition the service |
| Transition cost for transfer to cloud (if known) |  | Enter total cost to transition the service |
| Annual Staff cost changes for co-location |  | Enter any changes to staff costs |
| Annual Staff cost changes for cloud provision |  | Enter any changes to staff costs |

### Custom Solutions

| Data Required | Enter data here | Notes |
| --- | --- | --- |
| Cost of any custom solution |  | Enter in £/year |

# Acronyms

CPU	Central processing unit

kW	kilowatt, unit of measurement of power

kWh	kilowatt hour, unit of measurement of energy consumption

PDU	Power Distribution Unit

PUE	Power Utilisation Efficiency

TCO	Total Cost of Ownership

UPS	Uninterruptible Power Supply

VDU	Visual display unit

W	Watt, unit of measurement of power

http://www.ibmsystemsmag.com/mainframe/Business-Strategy/ROI/energy_estimating/